## Hot work permit
Hot work permit
Permit no.
Date
Location
Time permit starts
Time permit ends
Hot work to be done
Person doing the work
Fire watch
Authorized by
Before the work starts
OSHA 1910.252 asks the person who authorizes cutting and welding to inspect the area and set the precautions, preferably in a written permit. Construction work has its own rules in 29 CFR 1926 Subpart J. Check the current text and your own program.
Area inspected by the person who authorizes the work
Combustibles moved at least 35 feet (10.7 m) from the work, or shielded with flameproof covers or guards
Floor swept clean for 35 feet, and wet or covered if it is combustible
Floor and wall openings, cracks and open doorways covered so sparks cannot drop or travel
Ducts and conveyors that could carry sparks protected or shut down
Combustible walls and partitions near the work shielded
No explosive atmosphere, and no work in an area where one could form
Used containers cleaned and vented before any heat is applied
Sprinklers in service, if the building has them
Fire extinguisher or hose ready for instant use
Fire watch assigned, trained and holding a fire extinguisher
Fire alarm location known to the welder and the fire watch
Special conditions
Anything specific to this job.
After the work
The fire watch stays for at least a half hour after welding or cutting stops, to catch smoldering fires.
Work finished (time) | Fire watch until (time) | Area checked by | Permit closed (initials)
A starting point. Adapt it to your equipment, your procedures and the rules that apply to you. Free template from portalbaseai.com